# Inspection Approval Note

## Background

The inspection of Boiler Unit B-07 was conducted on 2026-09-05 by Demo Inspector. The inspection is part of the routine maintenance schedule, which requires an operating pressure not exceeding 12 bar during routine operation. According to SOP-101: Boiler Pressure Inspection, Clause 4.2, any reading above 12 bar for more than 5 minutes must be logged as a non-conformity and escalated to the shift engineer within 1 hour. The inspection frequency is every 90 days, as per Clause 4.4.

## Observations

The operating pressure of Boiler Unit B-07 was recorded as 13.2 bar.

## Non-Conformities

The operating pressure of 13.2 bar exceeds the maximum allowable pressure of 12 bar as specified in SOP-101: Boiler Pressure Inspection, Clause 4.2. This reading was recorded and must be escalated to the shift engineer within 1 hour as per Clause 4.3.

## Recommendation

Immediate action is required to address the non-conformity. The shift engineer should be informed within 1 hour, and the maintenance team should be notified to investigate and rectify the issue. The maintenance log should be updated with the details of this non-conformity, including the date, time, and inspector's name.

Generated locally by Sovereign AI Workbench